## 1. Contents
Wastewater Screening Calculations - S.I. Units
Workbook Contents
| Click on tabs at the bottom of the screen to access the following: |  | NOTE: The cells containing formulas are locked (protected) to avoid the
possibility of inadvertently typing over any of the formulas. You may,
|  | Tab 1. Contents (current tab) | however, adjust the number of decimal places for any of the cells.
Tab 2. Head Loss Through Bar Screens
|  | Tab 3. Head Loss Through Fine Screens | Introduction to the Wastewater Screening Calculations worksheets in this workbook:
|  | Tab 4. Screening Volume - Bar Screens | The second worksheet in this Wastewater Screening Calculations workbook is set up to calculate
the headloss for flow through a bar screen based on the design value of the wastewater flow rate
|  | Tab 5. Screening Volume - Fine Screens | and the bar screen spacing. The third worksheet is set up to calculate the head loss for flow through
a fine screen based on the design value of the wastewater flow rate and the diameter of the fine
screen perforations. The fourth worksheet is set up to calculate an estimate of the daily rate of
screenings collected by a bar screen based on the design value of the wastewater flow rate and the
| Copyright © McGraw-Hill, All rights reserved. |  | bar spacing. The fifth worksheet is set up to calculate an estimate of the daily rate of screenings
collected by a fine screen based on the design value of the wastewater flow rate and the diameter
of the fine screen perforations.

## 2. Head Loss Thru Bar Screens
| Wastewater Screening Calculations - S.I. Units | [6 empty] | References and Equations
|  | Calculation of Head Loss Across Bar Screen |  |  |  |  | For background and descriptive information about Wastewater Screening see:
Enter values in
USER INPUTS | a) Calculation of depth of flow for specified approach channel width and slope |  |  |  |  | yellow cells only | Introduction to Water Resource Recovery Facility Design, 2nd Ed.
Ch. 4 Preliminary Treatment - Sec. 2.0 Screening
| Design Average | [5 empty] | Handbook of Environmental Engineering Calculations, 2nd Ed.
| Infl. Flow Rate, Q = | 7570 | m3/d | Manning roughness, n = | 0.013 |  | 1.7 Wastewater Engineering - Sec. 14 Screening Devices
Channel
| bottom slope, S = | 0.0008 | m/m | Channel Width, b = | 0.45 | m | Water and Wastewater Calculations Manual, 3rd Ed.
Ch. 6 Wastewater Engineering - Sec. 14 Screening Devices
|  |  | Initial assumed depth of flow, y = |  | 0.34 | m
| Note that an initial assumed value of depth of flow is needed here to start the iterative calculation below. | [5 empty] | Information about the Manning Equation, used to calculate the depth of flow in the approach channel
[7 empty] | is available at: | Open Channel Hydraulics, 3rd Ed, Sec. 4.4 Background of the Chezy and Manning Formulas
CALCULATIONS
| Infl. Flow Rate, Q = | 0.087616 | m3/s | Area of Flow, A = | 0.153 | m2 | The Manning Equation: Q = (1.0/n)(A)(R2/3)(S1/2) is given as:
| (in m3/s) | [7 empty] | Equation 7.34 in the Handbook of Hydraulics, 8th Ed.
| Q*n/(1.0*S1/2) = | 0.04027 |  | Wetted Perimeter, P = | 1.13 | m
The values for the Manning Roughness Coefficient, n, in the tables below are from:
| A*R2/3 = | 0.040343 |  | Q*n/(1*S1/2) - A*R2/3 = | -7.2972e-05 |  |  |  | Open Channel Hydraulics, 3rd Ed., Table 4.1
Depth of Flow for channel
| parameter values shown above = |  |  | 0.34 | m
NOTE: Use Excel's "Goal Seek" to find y as follows: Place the cursor on cell G21 and click on
"Goal Seek" (in the "tools" menu of older versions and under "Data - What if Analysis" in newer
versions of Excel). Enter values to "Set cell:" G21, "To value:" 0, "By changing cell:" G13, and
click on "OK". The calculated value of y will appear in cells G13 and F 23 above. Cell G21 should
equal zero if the process worked properly. Note that an initial estimate of y is needed in cell G13
to start the iterative process.
USER INPUTS | b) Calculation of head loss across bar screen
Coefficient
| of Discharge, C = | 0.84 |  | Number of Bars, NB = | 6
The equation used to calculate the headloss across a bar screen is: hL = (1/C2)[(Vs2 – V2)/2g]
| Width of Bars, WB = | 25.12 | mm |  |  |  | This is: | Equation 6-29 in Water and Wastewater Calculations Manual, 3rd Ed.
[7 empty] | The parameters in Equation 6-29 are: |  | hL = headloss across bar screen, m
C = discharge coefficient (a typical value is 0.84)
CALC'NS | [8 empty] | Vs = velocity through bar screen, m/s
V = approach velocity in channel, m/s
|  |  |  | Velocity thru Screen, Vs = | 0.86104 | m/s
| Approach Velocity, V = | 0.57265 | m/s
|  |  | Headloss across Screen, hL = |  | 0.029866 | m
Copyright © McGraw-Hill, All rights reserved.
0
1/8
1/4
3/8
1/2
5/8
3/4
7/8

## 3. Head Loss Thru Fine Screens
| Wastewater Screening Calculations - S.I. Units | [6 empty] | References and Equations
| Calculation of Head Loss Across Perforated Fine Screen | [5 empty] | For background and descriptive information about Wastewater Screening see:
Introduction to Water Resource Recovery Facility Design, 2nd Ed.
INPUTS |  | Enter vaues in yellow cells only |  |  |  |  | Ch. 4 Preliminary Treatment - Sec. 2.0 Screening
Handbook of Environmental Engineering Calculations, 2nd Ed.
| Design Average |  |  | Coefficient |  |  | 1.7 Wastewater Engineering - Sec. 14 Screening Devices
| Infl. Flow Rate, Q = | 7570 | m3/d | of Discharge, C = | 0.6
| No. of Perforations in |  |  | Diameter |  |  | Water and Wastewater Calculations Manual, 3rd Ed.
| Submerged Screen, N = | 400 |  | of Perforations, DP = | 6 | mm | Ch. 6 Wastewater Engineering - Sec. 14 Screening Devices
The equation used to calculate the headloss across a fine screen is: h = (1/2g)(Q/CA)2
CALC'NS | [6 empty] | This is: | Equation 6-32 in Water and Wastewater Calculations Manual, 3rd Ed.
|  |  |  | Submerged |  |  | The parameters in Equation 6-32 are: |  | h = headloss across screen, m
| Infl. Flow Rate, Q = | 0.087616 | m3/s | Open Area, AO = | 0.01131 | m2 |  |  | C = coefficient of discharge for the screen
| (in cfs) | [7 empty] | (a typical value of C for a clean screen is 0.60)
g = gravitational acceleration, m/s2
| Headloss across screen, hL = |  |  | 8.4969 | m |  |  |  | Q = discharge through the screen, m3/s
A = area of effective opening of submerged screen, m2
Copyright © McGraw-Hill, All rights reserved.

## 4. Screening Vol. - Bar Screens
| Wastewater Screening Calculations - S.I. Units | [6 empty] | References and Equations
| Calculation of Screenings Volume for Bar Screen | [5 empty] | For background and descriptive information about Wastewater Screening see:
Introduction to Water Resource Recovery Facility Design, 2nd Ed.
INPUTS |  | Enter vaues in yellow cells only |  |  |  |  | Ch. 4 Preliminary Treatment - Sec. 2.0 Screening
Handbook of Environmental Engineering Calculations, 2nd Ed.
[7 empty] | 1.7 Wastewater Engineering - Sec. 14 Screening Devices |  |  |  |  | 10 | 0.24 | 0.24003
| Design Average |  |  | Width of Openings | [7 empty] | 20 | 0.16 | 0.16006
| Infl. Flow Rate, Q = | 7570 | m3/d | between Bars, Wo = | 34.3 | mm | Water and Wastewater Calculations Manual, 3rd Ed. |  |  |  |  | 40 | 0.08 | 0.080112
[7 empty] | Ch. 6 Wastewater Engineering - Sec. 14 Screening Devices |  |  |  |  | 50 | 0.06 | 0.060125
[7 empty] | Design of Water Resource Recovery Facilities, 6th Ed. - Figure 9.1 |  |  |  | will be used to
calculate the head loss across a bar screen with specified width between bars.
CALC'NS | Estimated Volume of Screenings Removed from Wastewater:
The values in the table below were read from Figure 9.1, which is shown below left.
| Estimated Minimum Volume, Vmin = |  | 0.095346 | L/1000 m3 or | 0.72177 | L/day
| Estimated Average Volume, Vave = |  | 0.27483 | L/1000 m3 or | 2.0805 | L/day | Screen | Min Screenings | Ave Screenings | Max Screenings
| Estimated Maximum Volume, Vmax = |  | 0.50925 | L/1000 m3 or | 3.855 | L/day | Opening, mm | Vol., L/1000 m3 | Vol., L/1000 m3 | Vol., L/1000 m3 |  | 10 | 0.37 | 0.36997
[7 empty] | 10 | 0.24 | 0.37 | 0.6 |  | 20 | 0.325 | 0.32498
[7 empty] | 20 | 0.16 | 0.325 | 0.55 |  | 40 | 0.26 | 0.26002
[7 empty] | 40 | 0.08 | 0.26 | 0.5 |  | 50 | 0.24 | 0.24005
| Estimated Volume of Screenings Removed from Wastewater: | [5 empty] | 50 | 0.06 | 0.24 | 0.47
Figure 9.1 Screenings quantities from coarse screens
From the graphs and equation fitting at the right:
Equation for Min. Screenings Vol.: y = - (1.6667 x 10-6)x3 + 0.00025x2 - 0.01433x + 0.36
Equation for Ave. Screenings Vol.: y = 0.0000417x2 - 0.00575x + 0.423
[7 empty] | Equation for Max. Screenings Vol.: y = 0.0000333x2 - 0.0051x + .645 |  |  |  |  | 10 | 0.6 | 0.59733
[12 empty] | 20 | 0.55 | 0.55632
[12 empty] | 40 | 0.5 | 0.49428
[12 empty] | 50 | 0.47 | 0.47325

## 5. Screening Vol.- Fine Screens
| Wastewater Screening Calculations - S.I. Units | [6 empty] | References and Equations
| Calculation of Screenings Volume for Bar Screen | [5 empty] | For background and descriptive information about Wastewater Screening see:
Introduction to Water Resource Recovery Facility Design, 2nd Ed.
INPUTS |  | Enter vaues in yellow cells only |  |  |  |  | Ch. 4 Preliminary Treatment - Sec. 2.0 Screening |  |  |  |  | 2 | 4.8 | 4.8
[7 empty] | Handbook of Environmental Engineering Calculations, 2nd Ed. |  |  |  |  | 3 | 4.9 | 4.9
[7 empty] | 1.7 Wastewater Engineering - Sec. 14 Screening Devices |  |  |  |  | 5 | 5.1 | 5.1
| Design Average |  |  | Diameter of screen | [7 empty] | 6 | 5.2 | 5.2
| Infl. Flow Rate, Q = | 7570 | m3/d | Openings, Do = | 1.4 | mm | Water and Wastewater Calculations Manual, 3rd Ed.
Ch. 6 Wastewater Engineering - Sec. 14 Screening Devices
[7 empty] | Design of Water Resource Recovery Facilities, 6th Ed. - Figure 9.2 |  |  |  | will be used to
calculate the head loss across a fine screen with specified opening size.
CALC'NS | Estimated Volume of Screenings Removed from Wastewater:
The values in the table below were read from Figure 9.2, which is shown below left.
| Estimated Minimum Volume, Vmin = |  | 4.74 | L/1000 m3 or | 35.8818 | L/day
|  |  | 9.842 | L/1000 m3 or | 74.5039 | L/day | Screen | Min Screenings | Ave Screenings | Max Screenings
| Estimated Maximum Volume, Vmax = |  | 19.85 | L/1000 m3 or | 150.2645 | L/day | Opening, mm | Vol., L/1000 m3 | Vol., L/1000 m3 | Vol., L/1000 m3 |  | 2 | 9.5 | 9.47
[7 empty] | 2 | 4.8 | 9.5 | 15 |  | 3 | 8.8 | 8.85
[7 empty] | 3 | 4.9 | 8.8 | 13 |  | 5 | 7.6 | 7.61
[7 empty] | 5 | 5.1 | 7.6 | 10 |  | 6 | 7 | 6.99
| Estimated Volume of Screenings Removed from Wastewater: | [5 empty] | 6 | 5.2 | 7 | 9
Figure 9.2 Screenings quantities from fine screens
From the graphs and equation fitting at the right:
Equation for Min. Screenings Vol.: y = 0.10x + 4.6
Equation for Ave. Screenings Vol.: y = - 0.62x + 10.71
Equation for Max. Screenings Vol.: y = - 1.5x + 17.75
[12 empty] | 2 | 15 | 14.75
[12 empty] | 3 | 13 | 13.25
[12 empty] | 5 | 10 | 10.25
[12 empty] | 6 | 9 | 8.75